## 시트1
Standby time in hours [h] |  | 1 | [13 empty] | emergencycurrenttime |  | Always on | 1/8
Alarm time in hours [h] |  | 0.25 | [13 empty] | alarmemergencycurrenttime |  | Only on for supervision | 1/3
Amplifier Mode |  | 2 | [13 empty] | amplifiermode |  | Always off | Full power
Burst ratio |  | 2 | [13 empty] | burstratio
Type | Order# | Device | Q'ty |  | standby |  | 1/8 |  | 1/3 |  | Full |  | Off
|  |  | Main | Backup | current | Total | current | Total | current | Total | current | Total | current | Total
2XH250 | 580221 | Power Amplifier 2XH250W/100V |  |  | 1.6 | 0 | 8.7 | 0 | 21.3 | 0 | 38.8 | 0 | 0 | 0
2XH500 | 580222 | Power Amplifier 2XH500W/100V |  |  | 2 | 0 | 19.3 | 0 | 40 | 0 | 86 | 0 | 0 | 0
2XD250 | 580231 | Power Amplifier 2XD250W/100V |  |  | 0.4 | 0 | 3.6 | 0 | 8.8 | 0 | 25 | 0 | 0.1 | 0
2XD400 | 580232 | Power Amplifier 2XD400W/100V | 6 |  | 0.5 | 3 | 5.6 | 33.6 | 13.9 | 83.4 | 40.5 | 243 | 0.1 | 0.6
DOM4-8 | 583361.22 | Digital Output Module DOM4-8 |  |  | 1 | 0 | 1.6 | 0 | 1.6 | 0 | 1.6 | 0 | 1 | 0
DOM4-24 | 583362.22 | Digital Output Module DOM4-24 | 3 |  | 1 | 3 | 1.8 | 5.4 | 1.8 | 5.4 | 1.8 | 5.4 | 1 | 3
SCU | 583381.22 | System Communication Unit SCU | 1 |  | 1 | 1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1 | 1
Switch | 583392 / 93 | Fiber Optic Ethernet Switch (Multi-/Singlemode) |  |  | 0.25 | 0 | 0.25 | 0 | 0.25 | 0 | 0.25 | 0 | 0.25 | 0
Additional
|  | Total |  |  |  | 7 |  | 40.2 |  | 90 |  | 249.6 |  | 4.6
|  |  | Standbypower |  |  | 4.84 | burst |  | 90
|  |  | standby time |  |  | 1 | alarm time |  | 0.25
|  |  | Sum |  |  | 4.84 |  |  | 22.5
|  |  | Total |  |  | 27.34
|  |  | mincapacity |  | 1.25 | 34.175 | accucapacity |  | 90
|  |  | 배터리 최대용량 |  |  |  | 전원반의 최대 용량 | [8 empty] | 105 | 150
|  |  | currentconsumption |  |  | 150 | maxcurrent |  | 100
[6 empty] | 1 |  |  | 1 | [5 empty] | 1 | 105 | 150
|  | 전원반 갯수 | accu1 |  |  | 1 | [8 empty] | 2 | 210 | 300
|  |  | j45 |  |  | 0.22783 | [8 empty] | 3 | 315 | 450
|  |  | k45 |  |  | 0
|  |  | k44 |  |  | 0.22783
|  |  | k43 |  |  | 0
|  | 105Ah 배터리 갯수 | accu2 |  |  | 2 |  | 105
|  | 150Ah 배터리 갯수 | accu3 |  |  | 0 |  | 0
[6 empty] | 65 | 105 | 150
[6 empty] | 0.43333 | 0.7